## Slide 1: Explaining the Unexpected: Early Analysis of the Fukushima Dai-ichi Fuel Pools
North Carolina Health Physics Society Chapter Meeting Raleigh, NC 6 October 2011
Andrew Sowder, Ph.D., CHP
Senior Project Manager
Used Fuel & HLW Management

## Slide 2: Fukushima Dai-Ichi: Applying Industry and Government Resources
Substantial early engagement among DOE/EPRI/INPO/NEI/NRC
Each organization focused on its core capabilities and role
Direct and indirect support to TEPCO/Japan
Integrated response to policy, regulatory and technical lessons learned underway
US Department of Energy
US Nuclear Regulatory Commission
Nuclear Energy Institute
Institute of Nuclear Power Operations
+ Utilities, Vendors, and International Organizations
Notes: Core cooling and containment assessment
Spent fuel pool evolution, criticality, and fuel degradation assessment and mitigation options
On- and off-site dose rate and contamination assessments
Spent fuel pool structural integrity assessment
Contamination “fixative” assessment
Stability guidance – core, containment, spent fuel pools

## Slide 3: U.S. Based Institutions - Event Response Role
Nuclear Energy Institute
Institute of Nuclear Power Operations
Leads industry communications to media, public, and government stakeholders and leads interface with federal government
Coordinates industry response to operational aspects of an event
Provides technical support to industry
Notes: INPO-NEI-EPRI is key interface: Receive over $200 million annually from Identical domestic members.
--each organization with different core competencies
--each organization with same core objective—success of commercial nuclear industry—good for country and global community
Federal Role is so important
-- Regulatory Function
-- Resource for enabling research that is not appropriate for industry
Leverage Global Talent – dozens of bi- and multi-lateral relationships—two examples
-- Niigata Chuetsu Oki earthquake –INPO, NEI and EPRI contacted by JANTI. Assisted in peer reviews, SMA and SPRA, restart criteria, ‘hidden damage’ methodologies, Fire Protection
-- JANTI organized Seismic Symposium at KK Site– Feb ’08 – TEPCO and
-- JANTI – Fire Protection Assessment and Design methods
EDF Materials Aging Institute

## Slide 4: EPRI Role / Industry Path Forward
Participation on “Industry Support Team”
Direct support for TEPCO by various EPRI groups
  Plant Technology
  Chemistry, LLW, RM
  Used Fuel & HLW, FRP
The Way Forward Initiative
www.nei.org/filefolder/TheWayForward_060611_FinalA2.pdf

## Slide 5: Industry Roles under “The Way Forward”

## Slide 6: Fukushima Dai-ichi Before 11 March 2011
Units 1 - 4
Units 5 - 6
Dry Storage
Common Fuel Pool

## Slide 7: Fukushima Dai-ichi After Tsunami
Source: TEPCO

## Slide 8: Fukushima Dai-ichi After Tsunami
Source: TEPCO

## Slide 9: 11 March Fukushima Dai-ichi Tsunami Strike

## Slide 10: 11 March Tsunami Strike at Fukushima Dai-ichi
Source: JNES

## Slide 11: Early Event Analysis
Accurate understanding essential for applying lessons learned
Early analysis drives focus on credible, significant issues
Understanding still evolving (incomplete data, many theories)
Focus for this Presentation:
What role, if any, did the fuel pools play in the events at Fukushima Dai-ichi?

## Slide 12: What is a Spent Fuel Pool?
Water-filled, stainless-steel-lined, concrete basin for storing irradiated fuel
Provides
  cooling
  radiation shielding
  sub-critical condition
Refueling every 18-24 months in US, 12-15 months in Japan
  reactor shutdown, vessel opened, and fraction of core replaced with fresh fuel
  used or spent fuel moved to pools
Pool provides large thermal inertial provided, but “young” used fuel requires substantial heat removal.

## Slide 13: Fukushima Dai-ichi Design
Source: NEI, 2011. http://www.nei.org/filefolder/BWR_illustration_3.jpg

## Slide 14: Fukushima Dai-ichi Fuel Pool
Source: TEPCO

## Slide 15: Spent Fuel Pool Details
Pool Elevations
Fuel Racks

## Slide 16: Used Fuel Management at Fukushima Dai-ichi
Storage method | Inventory as of March 2010 | Total Capacity
 | # Assemblies | 
Spent fuel pool at each reactor unit | 3,450 | 8,310
Dry cask | 408 | 408
Common pool | 6,291 | 6,840
Total | 10,149 | 15,558
Source: TEPCO

## Slide 17: Fukushima Dai-ichi Fuel Pool Inventories
 | Reactor Power Level (MWt/MWe) | Core Fuel Assemblies | Most Recent Addition of Irradiated Fuel to Pool | Irradiated fuel Assemblies in Pool | Unirradiated fuel Assemblies in Pool | Total Number of Assemblies in the Pool | Pool Assembly Capacity | Pool Decay Power (MW)
Unit 1 | 1380/460 | 400 | March 2010 | 292 | 100 | 392 | 900 | 0.07
Unit 2 | 2381/784 | 548 | Sept 2010 | 587 | 28 | 615 | 1,240 | 0.5
Unit 3 | 2381/784 | 548 | June 2010 | 514 | 52 | 566 | 1,220 | 0.2
Unit 4 | 2381/784 | 0 | Nov 30, 2010 | 1,331 | 204 | 1,535 | 1,590 | 2.3
Unit 5 | 2381/784 | 548 | Jan 2010 | 946 | 48 | 994 | 1,590 | 0.8
Unit 6 | 3293/1100 | 764 | Aug 2010 | 876 | 64 | 940 | 1,770 | 0.7
Common Pool | - | - | - | 6,375 | - | 6,375 | 6,840 | 1.2

## Slide 18: 1F4 Fuel Pool Map Indexed by Assembly Thermal Power

## Slide 19: Understood: Hydrogen Explosions in Units 1 and 3
Zr + 2H2O → ZrO2 + 2H2 + energy

## Slide 20: Unexpected: 15 March Unit 4 Damage
Source: Air Photo Service Co. Ltd., Japan

## Slide 21: Early Focus on 1F Unit 4 Pool
Damage to Unit 4 reactor building unexpected
  Unit 4 reactor was offline for maintenance
  Defueled ~100 days before earthquake/tsunami
Full core offload in fuel pool
  youngest, hottest fuel (2.3 MW decay heat load in 1F4 pool vs. <1 MW in other pools)
  most reactive fuel (first cycle for BWR)
  other pools less challenged
BEFORE
AFTER

## Slide 22: March 16: Grave Statements from US Officials
http://abcnews.go.com/Business/wireStory?id=13150227

## Slide 23: Rampant Speculation on Cause of Unit 4 Damage
Hydrogen gas from spent fuel in pool from high temp reaction of steam w/ Zr cladding after loss of water
Hydrogen gas from :
  radiolysis (radiation induced breakdown of H2O)
  other sources in Unit 4
  Unit 3 shared piping or other connectivity
Other combustible gas in Unit 4
Combustion of soot from lube oil fire
Venting of hydrogen gas from Zr oxidation in Unit 1 and 3 cores implicated in explosions of those units.
Zr + 2H2O → ZrO2 + 2H2 + energy

## Slide 24: Early Information for Unit 4 Assessment
15 March - Unit 4 explosion at day 4 (<< nominal time for boil off)
Ongoing venting of Unit 1 – 3 containments
Increasing flow of dose rate and environmental data
  early exposure readings in vicinity of Unit 4 building
  contamination of sea water near plant
  low (near ambient) Pu soil concentrations onsite
Unconfirmed reports of water in pool
Initial water spray from ground level on 20 March
Water additions via concrete pump boom on 22 March
12 April – Water sample collected, water temp (90 ºC) & level (2 m above fuel), dose rate measured prior to filling*
3/17 dose rates:
87.7 mSv/hr at 100 m el.
400 mSv/hr near Unit 3 west wall
100 mSv/hr near Unit 4
*Reported to be “several dozens” of mSv/hr above refueling floor – consistent with water above fuel.

## Slide 25: Lots of Unfiltered Information

## Slide 26: Milestone: 13 April 2011 Water Analysis Data for Unit 4 Pool
Unit 4 fuel pool water analysis
Unit 2 fuel pool water analysis
Data Source: TEPCO

## Slide 27: Reported Water Additions to 1F4 Consistent with Evaporation – Not Leakage
TEPCO concludes on 4/28 fuel pools not leaking based on daily evaporation rates of 140 to 210 tons (kiloliters) of water daily that match water additions.

## Slide 28: Milestone: Underwater Images of Unit 4 Pool Conditions
No damage to storage structure
No major fuel damage
Source: TEPCO

## Slide 29: Closing in on Cause for Unit 4 Damage
Other Unit 4 sources of hydrogen or other combustible material not considered significant or credible
Unit 3 as source of hydrogen remains most credible suspect
  timing of Unit 3 & 4 events
  hydrogen role in Units 1 & 3 damage
  shared vent stack and piping
  consistent failure of venting
  16 May TEPCO analysis
Hydrogen from Unit 3 currently most credible theory.
Visual evidence of fuel, racks, and pool integrity does not support catastrophic pool drainage and Zr oxidation event
Source: Air Photo Service Co. Ltd., Japan

## Slide 30: TEPCO 16 May 2011 Theory for Source of Hydrogen in Unit 4
Source: TEPCO

## Slide 31: TEPCO 16 May 2011 Theory for Source of Hydrogen in Unit 4 (cont’d)
Source: TEPCO

## Slide 32: 1F4 Emergency Gas Treatment System – Post Accident Configuration
Source: TEPCO
27 August 2011

## Slide 33: June 15: The Correction
http://abcnews.go.com/US/wireStory?id=13845733

## Slide 34: Interim EPRI Assessments
Fukushima Dai-ichi Fuel Pool Criticality Assessment
Summary of fuel pool evolution following loss of cooling
  preliminary gap analysis
  calculation of time required to evaporate 1F fuel pool water inventory for key scenarios
  identifying important scenarios and mitigating factors
Evaluation of proposed scenarios directly implicating Unit 4 pool in hydrogen generation
  from cladding oxidation in blocked fuel channels experiencing DNB in a pool with water level above fuel
  from enhanced radiolysis in high radiation fields in a fuel pool at or near boiling

## Slide 35: Early EPRI Criticality Assessment for Fukushima Dai-ichi Fuel Pools
A spent fuel pool criticality event remains highly unlikely in damaged Fukushima Dai-ichi spent fuel pools.
  includes the extreme case of the introduction of water to a dry fuel pool
  total fuel inventory present in the form of rubblized fuel pellet fragments lying at the bottom of the pool
Primary objective for mitigation of drained fuel pool at Fukushima should be covering spent fuel pool with water to reduce the dose to workers.
Notes: This summary was shared with INPO, TEPCO, and NRC.
One page summary touching on 5 key considerations.
Aligned with preliminary ORNL Assessment provided to NRC on 18 March 2011:
“Our opinion is that criticality in the spent fuel pools is very unlikely, particularly if boron is being used, and that, if other information is correct, such as the water level in the pool at unit 4 is very low (or empty), the consequences of criticality in one of the spent fuel pools will not be significant in comparison to the consequences of the pool remaining empty/exposed. As a reminder to all, these are BWR spent fuel pools, and hence did not have borated water in them to begin with. These are our personal/professional opinions, based on the information available to us at this time, and should be treated as such.”

## Slide 36: Fuel Pool Evolution Following Loss of Cooling
The level of water at which temperatures start ramping up will depend on decay heat and assumed heat transfer mechanisms, including boiling heat transfer at the submerged fuel rod-water interface.
GAP: More realistic assessment of the transition point from sufficient to insufficient axial cooling as a function of rack and assembly design and decay heat.
Stage | Sequence
1 | Nominal condition of pool: 30-45°C, normal water level
2 | Pool water temperature gradually approaches water boiling point
3 | Boiling of pool water: Boiling begins in racks where hottest fuel assemblies are stored; pool water level gradually decreases towards top of fuel assemblies’ levels
4 | Gradual uncovering of fuel assemblies
5 | Thermal ramping of fuel rods in the presence of water (water level above rack base plate).
6 | Thermal ramping of fuel rods in the absence of water (pool water below rack base plate).
7 | Dispersal of fuel materials

## Slide 37: Estimated Time Margins for 1F Pools Based on Simple Calculations
NOTE: For Unit 4, additional inventory from refueling cavity and D/S pit could provide up to 14 days of additional margin.
Assumes:
Initial Pool Temp = 35 °C
Initial sloshing removes 1.5 m of water inventory

## Slide 38: TEPCO 20 June 2011 Theory for Evolution of 1F4 Fuel Pool Water Inventory following LOCA
Refueling well and D/S pit were flooded and interconnected.
Spent fuel pool gate was in place.
Following evaporation of pool inventory, leakage from adjoining refueling cavity provided an alternative source of makeup water

## Slide 39: Early EPRI Evaluation of Scenarios Implicating Fuel Pool in Unit 4 Explosion
Hydrogen generation from cladding oxidation in pool with water covering fuel due to localized departure from nuclear boiling (DNB) in debris-blocked fuel channels
Hydrogen from water radiolysis in 1F4 storage pool (fuel offload)
Hydrogen from zircaloy cladding oxidation not likely for pool levels covering at least half the fuel height
Bounding production rate calculations indicate insignificant H2 production relative to building volume to cause explosion (<<1% in gas mixture)

## Slide 40: Status of Unit 3 Fuel Pool
14 March: Unit 3 explosion
Source: TEPCO; Video image obtained 8 May 2011
Source: NHK
Data Source: TEPCO
13 April – Unit 3 pool reported to be “full”
Source: Air Photo Service Co. Ltd., Japan

## Slide 41: Status of Units 1 & 2 Fuel Pools
No video or photographic images of either pool
Unit 2 pool had 2nd highest thermal load (0.5 MW)
Unit 2 water additions start 3/20
Unit 2 fuel pool water analysis
Data Source: TEPCO
Source: Air Photo Service Co. Ltd., Japan
Notes: 160,000 Bq ~ 4 uCi

## Slide 42: Units 1 - 4 Summary as of 16 August 2011
Source: TEPCO

## Slide 43: Units 1 - 4 Summary as of 16 August 2011
Structure reinforcement of Unit 4 pool completed
Hydrazine has been added to Units 2, 3, 4 for corrosion concerns
Boric acid has been added to Unit 3 for pH purposes
A truck-mounted desalination unit is being planned for CL- reduction; movable between units; not in service as of 8/15/11
Unit 3 water sample of 5/9/11 showed CL- at 2,400 ppm and pH 11.2
ND - Not Detectable
Source: TEPCO

## Slide 44: Status of Fuel in Dry Storage and Common Pool
17 March - While also inundated with water, TEPCO confirms integrity of dry storage casks and building
18 March - TEPCO confirms stability of common fuel pool
Source: TEPCO

## Slide 45: Broader Picture: Event Analysis ► Understanding ► Lessons Learned
U.S. plant features and operating practice have evolved in light of operating experience and knowledge
Still early in Fukushima recovery phase
Event analysis remains incomplete
Implications for U.S. plant design and operations not fully understood
Post-Fukushima:
  vulnerabilities identified and corrected
  mitigation strategies developed for credible beyond design basis hazards
Post 9/11 or B.5.B Mitigation Strategies
TMI Modifications
IPE / IPEEE and PRA Modifications
Design Basis Accidents
Fukushima Strategies
All Hazard Risks
Mitigation

## Slide 46: Post-Fukushima R&D Path Forward
Verify current understanding
Identify and address gaps
  Risks posed by external hazards
  Severe accident progression, including combustible gas control
  Monitoring and instrument needs
  Radiological releases and paths
  Fuel pool phenomena and relative risk
  Integration and execution of mitigation actions
Establish and preserve pedigreed Fukushima accident knowledge base
Notes: Requires Prospective analysis of the unimaginable
Apply Fukushima filter to:
Conduct internal EPRI assessment
Integrate external member input
Modify strategic roadmaps as necessary
Review re-prioritization recommendations with NPC
Make adjustments to portfolio
provide direction to develop response actions
  Ensure long term viability of emergency response equipment, procedures and training
  Coping strategies well synchronized to ensure core cooling, containment integrity and spent fuel cooling
  Strategies must be symptom-based and applied to multiple units
  Strategies should consider prevention, coping and mitigation to optimize timeliness and resource allocation

## Slide 47: Together…Shaping the Future of Electricity